## gen
unit label | P_max (MW) | Q_max (MVAR) | Q_min (MVAR) | fuel | full load heat rate (Btu/kWh) | fixed O&M (1979$/kW/year) | variable O&M (1979$/MWh) | fixed O&M (2015$/kW/year) | variable O&M (2015$/MWh) | (based on http://data.bls.gov/cgi-bin/cpicalc.pl)
U12 | 12 | 6 | 0 | residual | 12000 | 10 | 0.9 | 32.8 | 2.952
U20 | 20 | 30 | -25 | distillate | 14500 | 0.3 | 5 | 0.984 | 16.4
U50 | 50 | 16 | -10 | hydro | . | 0 | 0 | 0 | 0
U76 | 76 | 30 | -25 | coal | 12000 | 10.5 | 0.9 | 34.44 | 2.952
U100 | 100 | 60 | 0 | residual | 10000 | 8.5 | 0.8 | 27.88 | 2.624
U155 | 155 | 80 | -50 | coal | 9600 | 7 | 0.8 | 22.96 | 2.624
U197 | 197 | 80 | 0 | residual | 9500 | 5 | 0.7 | 16.4 | 2.296
U350 | 350 | 150 | -25 | coal | 9500 | 4.5 | 0.7 | 14.76 | 2.296
U400 | 400 | 200 | -50 | nuclear | 10000 | 5 | 0.3 | 16.4 | 0.984
SyncCond | 200 | 200 | -50 | sync_cond | . | 0 | 0 | 0 | 0
O&M based on 1979 IEEE RTS as reported in Billinton and Li 1994
from 1999 IEEE RTS
heat rate breakpoints (and min load)
unit label | output (%) | heat rate (Btu/kWh) | total fuel | incremental rate
U12 | 0.2 | 16017 | 3203.4 | 10155.3333
U12 | 0.5 | 12500 | 6250 | 10900
U12 | 0.8 | 11900 | 9520 | 12400
U12 | 1 | 12000 | 12000
U20 | 0.79 | 15063 | 11899.77 | 10023
U20 | 0.8 | 15000 | 12000 | 12500
U20 | 1 | 14500 | 14500
U76 | 0.2 | 17107 | 3421.4 | 9657
U76 | 0.5 | 12637 | 6318.5 | 10671.6667
U76 | 0.8 | 11900 | 9520 | 12400
U76 | 1 | 12000 | 12000
U100 | 0.25 | 12999 | 3249.75 | 8401
U100 | 0.5 | 10700 | 5350 | 9065.3333
U100 | 0.8 | 10087 | 8069.6 | 9652
U100 | 1 | 10000 | 10000
U155 | 0.35 | 11244 | 3935.4 | 8385.6
U155 | 0.6 | 10053 | 6031.8 | 8713
U155 | 0.8 | 9718 | 7774.4 | 9128
U155 | 1 | 9600 | 9600
U197 | 0.35 | 10200 | 3570 | 8760
U197 | 0.6 | 9600 | 5760 | 9200
U197 | 0.8 | 9500 | 7600 | 9500
U197 | 1 | 9500 | 9500
U350 | 0.4 | 10200 | 4080 | 8385.6
U350 | 0.65 | 9600 | 6240 | 8713
U350 | 0.8 | 9500 | 7600 | 9128
U350 | 1 | 9500 | 9500
U400 | 0.25 | 12751 | 3187.75 | 8385.6
U400 | 0.5 | 10825 | 5412.5 | 8713
U400 | 0.8 | 10170 | 8136 | 9128
U400 | 1 | 10000 | 10000
fuel costs | *** get these from EIA averages for 2013 or 2014
fuel | cost (1979$/MMBtu) | cost (2015$/mmBtu) | (based on http://data.bls.gov/cgi-bin/cpicalc.pl)
residual | 2.3 | 7.544
distillate | 3 | 9.84
coal | 1.2 | 3.936
nuclear | 0.6 | 1.968
generator projects
load_zone | bus | unit type | unit id | project id | unit index
A | 1 | U350 | 1 | U350_1 | 8
A | 2 | U350 | 1 | U350_2 | 8
hydro limits
month | power limit (%) | energy limit (%) | max power (MW) | max energy (MWh/day)
12 | 0.9 | 0.2 | 45 | 438.3562
hydro projects
row
0 | project id
#N/A | #N/A
#N/A | #N/A
#N/A | #N/A
#N/A | #N/A
#N/A | #N/A
#N/A | #N/A
#N/A | #N/A
#N/A | #N/A
#N/A | #N/A
hydro project limits
project | timeseries | max power | max energy
#N/A | 2015 | 45 | 438.3562
#N/A | 2015 | 45 | 438.3562
#N/A | 2015 | 45 | 438.3562
#N/A | 2015 | 45 | 438.3562
#N/A | 2015 | 45 | 438.3562
#N/A | 2015 | 45 | 438.3562

## load
Peak Bus Loads
load_zone | bus | MW | MVAr
A | 3 | 200 | 20
Hourly Peak Load in Percentage of Daily Peak (weekday, peak week (51))
hour | load (%)
0 | 0.5
12 | 0.9
hourly loads by bus
bus row | hour_row | load_zone | bus | hour | load_MW | load_MVAr
1 | 1 | A | 3 | 0 | 100 | 10
1 | 2 | A | 3 | 12 | 180 | 18

## bus
bus | bus_load_zone | bus_v_setpoint_pu | bus_type | bus_g_mw | bus_b_mvar | bus_area | bus_base_kv | bus_loss_zone | bus_v_max_pu | bus_v_min_pu
1 | A | 1.035 | 3 | 0 | 0 | 11 | 138 | 1 | 1.05 | 0.95
2 | A | 1.035 | 2 | 0 | 0 | 11 | 138 | 2 | 1.05 | 0.95
3 | A | . | 1 | 0 | 0 | 11 | 138 | 1 | 1.05 | 0.95

## branch
branches |  | note: r, x, b data from IEEE ref system 1979 (same as 1999 but with more decimal places), via matpower and pypower; rest are from 1999 RTS
branch_id | contingency | fbus | tbus | r (pu) | x (pu) | b (pu) | normal rating | long term emergency rating | short term emergency rating | tap ratio | angle | status | angmin | angmax
A_1_3 | 1 | 1 | 3 | 0.0546 | 0.2112 | 0.0572 | 225 | 208 | 220 | 0 | 0 | 1 | -360 | 360
A_2_3 | 0 | 2 | 3 | 0.0546 | 0.2112 | 0.0572 | 225 | 208 | 220 | 0 | 0 | 1 | -360 | 360
A_1_2 | 0 | 1 | 2 | 0.06 | 0.3 | 0.05 | 70 | 208 | 220 | 0 | 0 | 1 | -360 | 360

## tab files
generator_info.tab
generation_technology | g_max_age | g_is_variable | g_is_baseload | g_is_flexible_baseload | g_is_cogen | g_competes_for_space | g_variable_o_m | g_energy_source | g_full_load_heat_rate | g_unit_size | g_q_max_mvar | g_q_min_mvar
U12 | 40 | 0 | 0 | 0 | 0 | 0 | 2.952 | residual | 12000 | 12 | 6 | 0
U20 | 40 | 0 | 0 | 0 | 0 | 0 | 16.4 | distillate | 14500 | 20 | 30 | -25
U50 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | hydro | . | 50 | 16 | -10
U76 | 40 | 0 | 0 | 0 | 0 | 0 | 2.952 | coal | 12000 | 76 | 30 | -25
U100 | 40 | 0 | 0 | 0 | 0 | 0 | 2.624 | residual | 10000 | 100 | 60 | 0
U155 | 40 | 0 | 0 | 0 | 0 | 0 | 2.624 | coal | 9600 | 155 | 80 | -50
U197 | 40 | 0 | 0 | 0 | 0 | 0 | 2.296 | residual | 9500 | 197 | 80 | 0
U350 | 40 | 0 | 0 | 0 | 0 | 0 | 2.296 | coal | 9500 | 350 | 150 | -25
U400 | 40 | 0 | 0 | 0 | 0 | 0 | 0.984 | nuclear | 10000 | 400 | 200 | -50
SyncCond | 40 | 0 | 0 | 0 | 0 | 0 | 0 | sync_cond | . | 200 | 200 | -50
fuel_cost.tab
load_zone | fuel | period | fuel_cost
A | residual | 2015 | 7.544
A | distillate | 2015 | 9.84
A | coal | 2015 | 3.936
A | nuclear | 2015 | 1.968
buses.tab
BUS | bus_load_zone | bus_v_setpoint_pu | bus_type | bus_g_mw | bus_b_mvar | bus_area | bus_base_kv | bus_loss_zone | bus_v_max_pu | bus_v_min_pu
1 | A | 1.035 | 3 | 0 | 0 | 11 | 138 | 1 | 1.05 | 0.95
2 | A | 1.035 | 2 | 0 | 0 | 11 | 138 | 2 | 1.05 | 0.95
3 | A | . | 1 | 0 | 0 | 11 | 138 | 1 | 1.05 | 0.95
project_info.tab
PROJECT | proj_gen_tech | proj_load_zone | proj_connect_cost_per_mw | proj_capacity_limit_mw | proj_bus
U350_1 | U350 | A | 0 | 350 | 1
U350_2 | U350 | A | 0 | 350 | 2
proj_existing_builds.tab
PROJECT | build_year | proj_existing_cap
U350_1 | 2015 | 350
U350_2 | 2015 | 350
hydro.tab
PROJECT | TIMESERIES | hydro_max_power_mw | hydro_max_energy_mwh
#N/A | 2015 | 45 | 438.3562
#N/A | 2015 | 45 | 438.3562
#N/A | 2015 | 45 | 438.3562
#N/A | 2015 | 45 | 438.3562
#N/A | 2015 | 45 | 438.3562
#N/A | 2015 | 45 | 438.3562
branches.tab
BRANCH | branch_contingency | branch_from | branch_to | branch_r_pu | branch_x_pu | branch_b_pu | branch_rating_mw_long_term | branch_rating_mw_short_term | branch_rating_mw_emergency | branch_tap_ratio | branch_phase_shift | branch_status
A_1_3 | 1 | 1 | 3 | 0.0546 | 0.2112 | 0.0572 | 225 | 208 | 220 | 0 | 0 | 1
A_2_3 | 0 | 2 | 3 | 0.0546 | 0.2112 | 0.0572 | 225 | 208 | 220 | 0 | 0 | 1
A_1_2 | 0 | 1 | 2 | 0.06 | 0.3 | 0.05 | 70 | 208 | 220 | 0 | 0 | 1
loads.tab
LOAD_ZONE | TIMEPOINT | lz_demand_mw
A | 0 | 100
A | 12 | 180
timepoints.tab
timepoint_id | timeseries
0 | 2015
12 | 2015
bus_loads.tab
BUS | TIMEPOINT | bus_demand_mw | bus_demand_mvar
3 | 0 | 100 | 10
3 | 12 | 180 | 18